Modbus Protocol

Setup via Modbus RTU for SERIAL Transmitters. Supported function codes, Registers table and examples.

Rev. 1.1 Jun 2017

- Introduction

This document describes how to set the address, baud rate, data format and read measured values from SERIAL devices with Modbus RTU interface.

Additionally it describes the data encoding of floating point values and the Modbus function codes supported by the SERIAL devices.

Contents

Introduction	1

1. Hardware interface	3

2. RS485 Slave ID, Baud rate, Data format	3

3. About Modbus (ref PI–MBUS–300)	3

4. Supported function codes	4

5. Data Encoding	4

6. Registers Table	5

Instrument Holding Registers	5

7. Data types	7

7-1 ASCII format	7

7-2 IEEE754 format	7

7-3 32-bit integer format	7

8. Communication Examples	8

8-1 Setting Slave ID	8

8-2 Setting Baud rate	8

8-3 Reading Temperature of floating point type	9

8-4 Reading Temperature of 32-bit integer type	9

8-5 Reading Relativity Humidity of floating point type	10

8-6 Reading Relativity Humidity of 32-bit integer type	10

8-7 Reading Serial No.	11

9. Revise history	12

# 1. Hardware interface

- The digital interface on the transmitter is RS485.

- Hardware named D+, D-

- Meet the standards TIA/EIA-485-A

# 2. RS485 Slave ID, Baud rate, Data format

- Slave ID: 1~247

- Baud rate: 9600, 19200, 38400, 57600, 115200

- Parity: None, Even, Odd

- Data length: 8 bit

- Stop bit: 1 or 2 bit

- Default Slave ID = 1, Data format= 9600, N81

# 3. About Modbus (ref PI–MBUS–300)

- Support RTU mode

- Broadcast support (Slave ID 0)

- Bit addressable items (i.e. Coils and Discrete inputs) will not be implemented

- Measured values are represented in two types

  - IEEE 754 single-precision 32-bit floating point type

  - 32-bit integer type, values are stored with a scaling of 1:100

- http://en.wikipedia.org/wiki/IEEE_754

- Modbus protocol structure:

- 1st byte: Slave ID (1~247)

- 2nd byte: Function code (1 byte)

- 3~Nth bytes: Data bytes

- N+1th~N+2th byte: CRC (16 bits), LSB first

# 4. Supported function codes

Following function codes are supported:

• 0x03 Read Holding Registers

• 0x06 Write Single Register

• 0x10 Write Multiple Registers

The measured values can be read by using 0x03 codes. The RS485 and unit can be set by using 0x06 or 0x10 code. The register numbers and the corresponding physical quantities are listed as below “Register Table”.

# 5. Data Encoding

SERIAL device uses a ‘big-Endian’ representation for addresses and data items. This means that when a numerical quantity larger than a single byte is transmitted, the most significant byte is sent first. So for example

Register size 	value

16 - bits 	0x1234	 	the first byte sent is 0x12 then 0x34

Register size 	value

32 - bits 	0x12345678	the first byte sent is 0x12 then 0x34, 0x56, 0x78

# 6. Registers Table

## Instrument Holding Registers

| Item No. | Register Address | Starting Address | Parameter | R/W | Data Bytes | Data Type | Value/ Unit |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Information |  |  |  |  |  |  |  |
| 1 | 40033 | 0x20 | Model Name | R | 16 bytes | ASCII |  |
| 2 | 40049 | 0x30 | Serial Number | R | 16 bytes | ASCII |  |
| 3 | 40065 | 0x40 | Firmware version | R | 16 byes | ASCII |  |
| RS485 Slave ID, Baud rate, Data format, Unit |  |  |  |  |  |  |  |
| 1 | 40081 | 0x50 | Slave ID | R/W | 1 bytes | unsigned Integer | 1 … 247 |
| 2 | 40083 | 0x52 | Baud rate | R/W | 1 bytes | unsigned Integer | 0: 9600 1: 19200 2: 38400 3: 57600 4: 115200 |
| 3 | 40085 | 0x54 | Data type | R/W | 1 bytes | unsigned Integer | 0: N81 1: N82 2: E81 3: E82 4: O81 5: O82 |
| 4 | 4087 | 0x56 | Unit | R/W | 1 byte | unsigned Integer | 0: Metric 1: Imperial |
| Physical Quantities |  |  |  |  |  |  |  |
| 1 | 41025 | 0x400 | Temperature | R | 4 bytes | Floating Pt. | ℃,°F |
| 2 | 41029 | 0x404 | Relative Humidity | R | 4 bytes | Floating Pt. | % |
| 3 | 41033 | 0x408 | Dew Point Temperature | R | 4 bytes | Floating Pt. | ℃,°F |
| 4 | 41037 | 0x40C | *Frost Point Temperature | R | 4 bytes | Floating Pt. | ℃,°F |
| 5 | 41041 | 0x410 | Wet Bulb Temperature | R | 4 bytes | Floating Pt. | ℃,°F |
| 6 | 41045 | 0x414 | Vapor Pressure | R | 4 bytes | Floating Pt. | mbar, psi |
| 7 | 41049 | 0x418 | Mixture Ratio | R | 4 bytes | Floating Pt. | g/kg, gr/lb |
| 8 | 41053 | 0x41C | Absolute Humidity | R | 4 bytes | Floating Pt. | g/m3 ,gr/ft3 |
| 9 | 41057 | 0x420 | Specific Enthalpy | R | 4 bytes | Floating Pt. | kJ/kg, BTU/lb |
| 10 | 41061 | 0x424 | PPMv | R | 4 bytes | Floating Pt. | ppm |
| 11 | 41065 | 0x428 | PPMw | R | 4 bytes | Floating Pt. | ppm |
| 12 | 41089 | 0x440 | Temperature | R | 4 bytes | **32-bit integer | ℃,°F |
| 13 | 41093 | 0x444 | Relative Humidity | R | 4 bytes | **32-bit integer | % |
| 14 | 41097 | 0x448 | Dew Point Temperature | R | 4 bytes | **32-bit integer | ℃,°F |
| 15 | 41101 | 0x44C | *Frost Point Temperature | R | 4 bytes | **32-bit integer | ℃,°F |
| 16 | 41105 | 0x450 | Wet Bulb Temperature | R | 4 bytes | **32-bit integer | ℃,°F |
| 17 | 41109 | 0x454 | Vapor Pressure | R | 4 bytes | **32-bit integer | mbar, psi |
| 18 | 41113 | 0x458 | Mixture Ratio | R | 4 bytes | **32-bit integer | g/kg, gr/lb |
| 19 | 41117 | 0x45C | Absolute Humidity | R | 4 bytes | **32-bit integer | g/m3 ,gr/ft3 |
| 20 | 41121 | 0x460 | Specific Enthalpy | R | 4 bytes | **32-bit integer | kJ/kg, BTU/lb |
| 21 | 41125 | 0x464 | PPMv | R | 4 bytes | **32-bit integer | ppm |
| 22 | 41129 | 0x468 | PPMw | R | 4 bytes | **32-bit integer | ppm |

* the maximum value of Frost Point is 0

** Values are stored with a scaling of 1:100 (e.g.: 2230 is equivalent to 22.3°C)

# 7. Data types

## 7-1 ASCII format

| 1st Word |  | 2nd Word |  | 3rd Word |  | 4th Word |  | 5th Word |  | 6th Word |  | 7th Word |  | 8th Word |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Hi byte | Lo byte | Hi byte | Lo byte | Hi byte | Lo byte | Hi byte | Lo byte | Hi byte | Lo byte | Hi byte | Lo byte | Hi byte | Lo byte | Hi byte | Lo byte |

“ABCDEF0123456789” is represented as <41><42><43><44><45><46><30><31><32><33><34><35><36><37><38><39>

## 7-2 IEEE754 format

| Data Hi Word, Hi Byte | Data Hi Word, Lo Byte | Data Lo Word, Hi Byte | Data Lo Word, Lo Byte |
| --- | --- | --- | --- |
| SEEE EEEE | EMMM MMMM | MMMM MMMM | MMMM MMMM |

Where

S 	represents the sign bit where 1 is negative and 0 is positive

E 	is the two’s complement exponent with an offset of 127 i.e. an exponent of zero is represented by

127, an exponent of 1 by 128 etc.

M 	is the 23-bit normal mantissa. The highest bit is always 1 and, therefore, is not stored.

Using the above format the floating point number 23.83 is represented as <41><BE><A3><D7>:

| Data Hi Word, Hi Byte | Data Hi Word, Lo Byte | Data Lo Word, Hi Byte | Data Lo Word, Lo Byte |
| --- | --- | --- | --- |
| 0x41 | 0xBE | 0xA3 | 0xD7 |

## 7-3 32-bit integer format

| Data Hi Word, Hi Byte | Data Hi Word, Lo Byte | Data Lo Word, Hi Byte | Data Lo Word, Lo Byte |
| --- | --- | --- | --- |
| 0x00 | 0x00 | 0x09 | 0x4F |

Number 22.3 is represented as <00><00><09><4F> in 32-bit integer type

# 8. Communication Examples

## 8-1 Setting Slave ID

Request from the host

| Slave ID | Function Code | Register Address |  | Register value |  | CRC |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 … 247 | 06 | 00 | 50 | 00 | 08 | CRC Lo | CRC Hi |

*setting Slave ID as 8

Response from the SERIAL devices

| Slave ID | Function Code | Register Address |  | Register value |  | CRC |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 … 247 | 06 | 00 | 50 | 00 | 08 | CRC Lo | CRC Hi |

* setting done, new Slave ID is 8

## 8-2 Setting Baud rate

Request from the host

| Slave ID | Function Code | Register Address |  | Register value |  | CRC |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 … 247 | 06 | 00 | 52 | 00 | 04 | CRC Lo | CRC Hi |

*setting baud rate as 115200

Response from the SERIAL devices

| Slave ID | Function Code | Register Address |  | Register value |  | CRC |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 … 247 | 06 | 00 | 52 | 00 | 04 | CRC Lo | CRC Hi |

* setting done, new baud rate is 115200

## 8-3 Reading Temperature of floating point type

Request from the host

| Slave ID | Function Code | Register Address |  | Number Of Registers |  | CRC |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 … 247 | 03 | 04 | 00 | 00 | 02 | CRC Lo | CRC Hi |

*Registers of Temperature floating type are 0x0400 ~ 0x0403

Response from the SERIAL devices

| Slave ID | Function Code | Byte Count | 2 Registers (4 bytes) |  |  |  | CRC |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 … 247 | 03 | 4 | 41 | B2 | 66 | 66 | CRC Lo | CRC Hi |

* the floating point number 22.3 is represented as <41><B2><66><66>

## 8-4 Reading Temperature of 32-bit integer type

Request from the host

| Slave ID | Function Code | Register Address |  | Number Of Registers |  | CRC |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 … 247 | 03 | 04 | 40 | 00 | 02 | CRC Lo | CRC Hi |

*Registers of Temperature floating type are 0x0440 ~ 0x0443

Response from the SERIAL devices

| Slave ID | Function Code | Byte Count | 2 Registers (4 bytes) |  |  |  | CRC |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 … 247 | 03 | 4 | 00 | 00 | 08 | B6 | CRC Lo | CRC Hi |

* the 32-bit integer number 22.3 is represented as <00><00><08><B6>

## 8-5 Reading Relativity Humidity of floating point type

Request from the host

| Slave ID | Function Code | Register Address |  | Number Of Registers |  | CRC |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 … 247 | 03 | 04 | 04 | 00 | 02 | CRC Lo | CRC Hi |

*Registers of Relativity Humidity floating type are 0x0404 ~ 0x0407

Response from the SERIAL devices

| Slave ID | Function Code | Byte Count | 2 Registers (4 bytes) |  |  |  | CRC |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 … 247 | 03 | 4 | 42 | 2E | CC | CD | CRC Lo | CRC Hi |

* the floating point number 43.7 is represented as <42><2E><CC><CD>:

## 8-6 Reading Relativity Humidity of 32-bit integer type

Request from the host

| Slave ID | Function Code | Register Address |  | Number Of Registers |  | CRC |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 … 247 | 03 | 04 | 44 | 00 | 02 | CRC Lo | CRC Hi |

*Registers of Relativity Humidity floating type are 0x0404 ~ 0x0407

Response from the SERIAL devices

| Slave ID | Function Code | Byte Count | 2 Registers (4 bytes) |  |  |  | CRC |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 … 247 | 03 | 4 | 00 | 00 | 11 | 12 | CRC Lo | CRC Hi |

* the 32-bit integer number 43.7 is represented as <00><00><11><12>

## 8-7 Reading Serial No.

Request from the host

| Slave ID | Function Code | Register Address |  | Number Of Registers |  | CRC |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 … 247 | 03 | 00 | 30 | 00 | 06 | CRC Lo | CRC Hi |

*Registers of Serial No. are 0x30 ~ 0x3F

Response from the SERIAL devices

| Slave ID | Function Code | Byte Count | 6 Registers (12 bytes) |  |  |  |  |  |  |  |  |  |  |  | CRC |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 … 247 | 03 | 0C | 53 | 4E | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | CRC Lo | CRC Hi |

*example of Serial No. is “SN0123456789”

# 9. Revise history

- v1.0 Step 2016	Initial edit

- v1.1 20170608	Add

PPMv_float(0x0424)

PPMw_float(0x0428)

PPMv_int(0x0464)

PPMw_int(0x0468)